## Sheet1
Device to Server
listener | 8884
type | Using pskKey, psk_file and password_file
QoS | 1
topic | PNEWELSv1/DeviceToApp/status/<muid>
Payload | {
"muid" : "<master id>"
"suid" : "<slave id>",
"gid" : "<group id>",
"ip" :"<ip address>" / "0.0.0.0",
"rssi" : "EXCELLENT" / GOOD" / "WEAK",
"mmode" : "STANDBY"/"EMERGENCY"/"MANUALTEST"/"DISCHARGETEST"/"LIGHTTEST"/”WIFISETTINGS”/"BATTERROR"/"ERROR"/”REBOOT”
"smode" : "STANDBY"/"EMERGENCY"/"MANUALTEST"/"DISCHARGETEST"/"LIGHTTEST"/"BATTERROR"/"ERROR"/"NOT CONNECTED"/”EMERGENCYACK”
"light" : "ON"/"OFF"/"ERROR",
"mbatt" : "LOW"/"NORMAL"/"ERROR",
"sbatt" : "LOW"/"NORMAL"/"ERROR",
}
Description : | Publish device status at predefined period. (Example: 50s)
muid : Unique Serial Number of master during factory mode programming.
suid : Unique Serial Number of slave during factory mode programming.
gid : Group ID to identify device model (Example : TEX300 / TTH311)
ip : Ip address of the device. will show 0.0.0.0 when it is not connected
rssi :
"EXCELLENT" - >= -60dbm
"GOOD" - >= -75dbm
"WEAK" - < -75dbm
mmode :
“STANDBY” - Charging and STANDBY
“EMERGENCY” - AC Power Failure
“MANUALTEST” - Test Button is pressed
“DISCHARGETEST” - Discharging Test
“LIGHTTEST” - Test Light On without EMERGENCY mode/Cutoff Wifi
“WIFISETTINGS” - AP Mode
“BATTERROR” - Battery Flat or disconnected
“ERROR” - System Error
“REBOOT” – to reboot wifi module
smode :
“STANDBY” - Charging and STANDBY
“EMERGENCY“ - AC Power Failure
“MANUALTEST“ - Test Button is pressed
“DISCHARGETEST“- Discharging Test
“LIGHTTEST“ - Test Light On without EMERGENCY mode/Cutoff Wifi
“BATTERROR“ - Battery Flat or disconnected
“ERROR“ - System Error
“NOT CONNECTED“ - slave not connected
“EMERGENCYACK” – mode reply from app after send EMERGENCY mode
light :
“ON” - Maintain Mode (TEX) - Light is detected during STANDBY / DISCHARGETEST - Non-maintain Mode (TTH) - Light is detected ON during DISCHARGETEST
“OFF” - Maintain Mode (TEX) - None - Non-maintain Mode (TTH) - Light is detected OFF during STANDBY
“ERROR” - Maintain Mode (TEX) - Light is NOT detected during STANDBY / DISCHARGETEST - Non-maintain Mode (TTH) - DISCHARGETEST
mbatt :
“LOW” - Battery Low and may Cutoff soon if Discharging (<2v0)
“NORMAL” - Battery is NORMAL(2v0 ~ 2v9)
“ERROR” - Battery is flat or disconnected
sbatt :
“LOW”- Battery Low and may Cutoff soon if Discharging (<2v0)
“NORMAL” - Battery is NORMAL(2v0 ~ 2v9)
“ERROR” - Battery is flat or disconnected
“FULL” - Battery is fully charged
Topic | PNEWELSv1/DeviceToApp/offline/<muid>
Payload | { "muid" : "<muid>" }
Description : | 1. To publish device offline/disconnected using MQTT WILL
muid : Unique Serial Number of master during factory mode programming.
Server To Device
listener | 8883
type | Certificate
QoS | 1
topic | PNEWELSv1/AppToDevice/command/direct/<muid>
Payload | {
"mcommand" : "LIGHTTEST"/"DISCHARGETEST"/"CHANGESSID" /"REBOOT"/"STANDBY"
"scommand" : "LIGHTTEST"/"DISCHARGETEST"/"STANDBY"/"EMERGENCYACK"
"ssidName" : "<ssid name>",
"ssidpassword" : "<ssid password>",
"brokerIP" : "<broker IP>",
}
Description : | muid : Unique Serial Number of master during factory mode programming.
mcommand :
“LIGHTTEST“ - Test Light
“DISCHARGETEST“ - Discharging Test
“CHANGESSID“ - Change Router and server settings and reboot itself
“REBOOT“ - Reboot itself
“STANDBY“ – Standby
scommand :
“LIGHTTEST“ - Test Light On
“DISCHARGETEST“ - Discharging Test
“STANDBY“ – Standby
“EMERGENCYACK“ - acknowlege emergency (send after PNEWELSv1/DeviceToApp/status/<uid> with status "EMERGENCY")
ssidName : Only needed during CHANGESSID command
ssidpassword : Only needed during CHANGESSID command
brokerIP : Only exists needed CHANGESSID command